## MK2
Year | kW/Cabinet | Installed Cabinets | Average PUE | Total load (MW) | Energy cost ($M) | Revenue ($M)
2025 | 4.9025 | 600 | 1.496 | 4.4005 | 7.7096 | 17.649
2026 | 5.3622 | 1200 | 1.492 | 10.4237 | 18.8102 | 42.7568
2027 | 5.9456 | 1800 | 1.488 | 18.1123 | 33.6652 | 75.9838
2028 | 6.5582 | 2400 | 1.484 | 27.5232 | 52.692 | 118.0911
2029 | 6.7385 | 2400 | 1.48 | 28.416 | 56.0333 | 124.6962
2030 | 6.8961 | 2400 | 1.476 | 28.3392 | 57.5583 | 127.1901
2031 | 7.0341 | 2400 | 1.472 | 28.2624 | 59.1244 | 129.7339
2032 | 7.1549 | 2400 | 1.468 | 28.1856 | 60.7326 | 132.3286
2033 | 7.2605 | 2400 | 1.464 | 28.1088 | 62.3841 | 134.9752
2034 | 7.3529 | 2400 | 1.46 | 28.032 | 64.0801 | 137.6747
2035 | 7.4338 | 2400 | 1.46 | 28.032 | 66.0025 | 140.4282
2036 | 7.5046 | 2400 | 1.46 | 28.032 | 67.9826 | 143.2367
2037 | 7.5665 | 2400 | 1.46 | 28.032 | 70.0221 | 146.1015
2038 | 7.6207 | 2400 | 1.46 | 28.032 | 72.1227 | 149.0235
2039 | 7.6681 | 2400 | 1.46 | 28.032 | 74.2864 | 152.004
2040 | 7.7096 | 2400 | 1.46 | 28.032 | 76.515 | 155.044
2041 | 7.7459 | 2400 | 1.46 | 28.032 | 78.8104 | 158.1449
2042 | 7.7777 | 2400 | 1.46 | 28.032 | 81.1748 | 161.3078
2043 | 7.8055 | 2400 | 1.46 | 28.032 | 83.61 | 164.534
2044 | 7.8298 | 2400 | 1.46 | 28.032 | 86.1183 | 167.8246
2045 | 7.8511 | 2400 | 1.46 | 28.032 | 88.7019 | 171.1811
2046 | 7.8697 | 2400 | 1.46 | 28.032 | 91.3629 | 174.6048
2047 | 7.886 | 2400 | 1.46 | 28.032 | 94.1038 | 178.0969
2048 | 7.9002 | 2400 | 1.46 | 28.032 | 96.9269 | 181.6588
2049 | 7.9127 | 2400 | 1.46 | 28.032 | 99.8347 | 185.292
2050 | 7.9236 | 2400 | 1.46 | 28.032 | 102.8298 | 188.9978
2051 | 7.9332 | 2400 | 1.46 | 28.032 | 105.9146 | 192.7778
2052 | 7.9415 | 2400 | 1.46 | 28.032 | 109.0921 | 196.6333
2053 | 7.9488 | 2400 | 1.46 | 28.032 | 112.3649 | 200.566
2054 | 7.9552 | 2400 | 1.46 | 28.032 | 115.7358 | 204.5773

## MK2 Modified
Year | kW/Cabinet | Installed Cabinets | Average PUE | Total load (MW) | Energy cost ($M) | Revenue ($M)
2025 | 6.885 | 160 | 1.444 | 5.9652 | 10.451 | 24.786
2026 | 7.7675 | 320 | 1.428 | 14.8226 | 26.7483 | 63.5256
2027 | 8.9456 | 480 | 1.412 | 26.9283 | 50.0515 | 119.0488
2028 | 10.2431 | 640 | 1.396 | 26.8032 | 51.3136 | 122.2512
2029 | 10.8408 | 640 | 1.38 | 26.496 | 52.2472 | 124.6962
2030 | 11.6745 | 640 | 1.364 | 26.1888 | 53.1907 | 127.1901
2031 | 12.737 | 640 | 1.348 | 25.8816 | 54.1438 | 129.7339
2032 | 14.0224 | 640 | 1.332 | 25.5744 | 55.1062 | 132.3286
2033 | 15.4746 | 640 | 1.316 | 25.2672 | 56.0775 | 134.9752
2034 | 17.1028 | 640 | 1.3 | 24.96 | 57.0576 | 137.6747
2035 | 18.7149 | 640 | 1.3 | 24.96 | 58.7694 | 140.4282
2036 | 20.3131 | 640 | 1.3 | 24.96 | 60.5324 | 143.2367
2037 | 21.8989 | 640 | 1.3 | 24.96 | 62.3484 | 146.1015
2038 | 23.4741 | 640 | 1.3 | 24.96 | 64.2189 | 149.0235
2039 | 25.0398 | 640 | 1.3 | 24.96 | 66.1454 | 152.004
2040 | 26.5973 | 640 | 1.3 | 24.96 | 68.1298 | 155.044
2041 | 28.1477 | 640 | 1.3 | 24.96 | 70.1737 | 158.1449
2042 | 29.6292 | 640 | 1.3 | 24.96 | 72.2789 | 161.3078
2043 | 30.9256 | 640 | 1.3 | 24.96 | 74.4473 | 164.534
2044 | 32.0599 | 640 | 1.3 | 24.96 | 76.6807 | 167.8246
2045 | 33.0524 | 640 | 1.3 | 24.96 | 78.9811 | 171.1811
2046 | 33.9208 | 640 | 1.3 | 24.96 | 81.3505 | 174.6048
2047 | 34.6807 | 640 | 1.3 | 24.96 | 83.791 | 178.0969
2048 | 35.3456 | 640 | 1.3 | 24.96 | 86.3048 | 181.6588
2049 | 35.9274 | 640 | 1.3 | 24.96 | 88.8939 | 185.292
2050 | 36.4365 | 640 | 1.3 | 24.96 | 91.5607 | 188.9978
2051 | 36.8819 | 640 | 1.3 | 24.96 | 94.3076 | 192.7778
2052 | 37.2717 | 640 | 1.3 | 24.96 | 97.1368 | 196.6333
2053 | 37.6127 | 640 | 1.3 | 24.96 | 100.0509 | 200.566
2054 | 37.9111 | 640 | 1.3 | 24.96 | 103.0524 | 204.5773

## 2022 set 1 (copy) (hidden)
Set 1 | [7 empty] | A |  |  | vs. |  |  | B
[6 empty] | Mk2 (current design) | [5 empty] | Mk2 Modified
| Input |  |  |  |  | Optimized for Air cooling, with min. hybrid cooling (Current) | [5 empty] | Optimized for liquid cooling, with min. air cooling (Proposed) | [5 empty] | Output | 10 | Years after Opening |  |  |  |  | Mk2 |  | Mk2 Modified
| Include = 'Y'; do not include = "N" | [6 empty] | Input slider | [6 empty] | Input slider |  |  | Include = 'Y'; do not include = "N" | [6 empty] | Air cooled optimized |  | Output
[8 empty] | Min. | Max. | [5 empty] | Min. | Max.
| Y | Cabinet ramp to 100%, years |  |  |  | 4 |  | 2 | 6 |  |  | 4 |  |  | 2 | 6 |  | Y | Average annual TUE (server fan power added to cooling power) | [5 empty] | #REF! |  | #REF!
| Y | Max. IT Load, MW |  |  |  | 19.2 |  | 10 | 40 |  |  | 19.2 |  |  | 10 | 40 |  | Y | Average annual PUE | [5 empty] | #REF! |  | #REF!
| Y | Max. number of cabinets |  |  |  | 2400 | [5 empty] | 640 | 25% | Uncertainty |  |  |  | Y | Annual power use, MWH | [5 empty] | #REF! |  | #REF! |  |  |  | Heat Rejection
| Y | Max. kW/cab (any given cab) |  |  |  | 10 | air cooled | 6 | 12 |  |  | 80 | liquid cooled |  | 40 | 100 |  | Y | GHG Emissions, Scope 1 |  |  | mtCO2e |  |  | #REF! |  | #REF! |  |  |  | Air
| Y | Min. kW/cab |  |  |  | 4 |  | 3 | 6 |  |  | 20 |  |  | 10 | 20 |  | Y | GHG Emissions, Scope 2 (market-based) |  |  | mtCO2e |  |  | #REF! |  | #REF! |  |  |  | Water
| Y | Max. Average kW/cab |  |  |  | 8 |  | 7 | 9 |  |  | 40 |  |  | 30 | 60 |  | Y | Relative Carbon metrics - Scope 3 |  |  | ratio |  |  | 100% |  | 56.86%
| Y | Years to go from Min. to Max.kW/cab |  |  |  | 8 |  | 4 | 10 |  |  | 20 |  |  | 4 | 10 |  | Y | Carbon Offset Against Local Grid Power |  |  | mtCO2e | (100% offset) |  | #REF! |  | #REF!
| Y | Start Year of Life |  |  |  | 2025 |  | 2023 | 2025 |  |  | 2025 |  |  | 2023 | 2025 |  | Y | Annual (local) water use for cooling |  |  | m3 per year | WCC/ACC/Heat pump |  | #REF! | <--WCC | 0 | <--ACC or Heat recovery heat pump
| Y | Total Life |  |  |  | 30 | [5 empty] | 30 | [5 empty] | Y | WUE |  |  | l/kWH |  |  | #REF! |  | #REF!
| Y | Air cooled %, Max. |  |  |  | 100% |  | 90% | 100% |  |  | 90% |  |  | 30% | 60% |  | Y | Net water metrics |  |  | m3 per year |  |  | #REF! |  | #REF!
| Y | Air cooled %, Min. |  |  |  | 90% |  | 60% | 90% |  |  | 50% |  |  | 5% | 20% |  | Y | Net space for all cabinets |  |  | KSF |  |  | 84 |  | 22.4
| Y | Typical location |  |  |  | Singapore | [5 empty] | Singapore | [5 empty] | Y | Gross space for all cabinets |  |  | KSF |  |  | 120 |  | 32
| Y | Heat rejection (Water or Air) |  |  |  | Air | [5 empty] | Air | [5 empty] | Y | Gross MEP space of data center |  |  | KSF |  |  | 84 |  | 84
| Y | % Heat recovery and reuse |  |  |  | 0% | [5 empty] | 80% |  |  | 0% | 100% |  | Y | Total data center area |  |  | KSF |  |  | 204 |  | 116
| Y | Peak PUE |  |  |  | #REF! | [5 empty] | #REF! |  |  | 1.05 | 1.15 |  | Y | Approximate capex |  |  | $M |  |  | 134.1716 |  | 105.5635
| Y | Annual PUE | (Lookup table) |  |  | #REF! | [5 empty] | #REF! | [5 empty] | Y | Energy cost first 10 years |  |  | $M |  |  | #REF! |  | #REF!
| Y | Server Fan Power (kW Fan/kW IT) |  |  |  | 10% |  | 4% | 20% |  |  | 3% |  |  | 0% | 5% |  | Y | Capex + energy cost first 10 years |  |  | $M |  |  | #REF! |  | #REF!
| Y | Annual TUE |  |  |  | #REF! |  | 1.5 | 1.7 |  |  | #REF! |  |  | 1.1 | 1.2 |  | Y | Revenue first 10 years |  |  | $M |  |  | 1046.0273 |  | 1096.6564
| Y | Years to go from Max. to Min. air cooled cab % |  |  |  | 10 |  | 5 | 10 |  |  | 10 |  |  | 5 | 10
| Y | Cabinet refresh x% of installed cabinets |  |  |  | 12.5% |  | 5% | 15% |  |  | 12.5% |  |  | 5% | 15%
| Y | Net space per Cabinet, SF |  |  |  | 35 |  | 25 | 40 |  |  | 35 |  |  | 25 | 40 |  | Output graphic formats should strive to show the impact of variations on input in a dynamic fashion.
| Y | Gross space per Cabinet, SF |  |  |  | 50 |  | 40 | 60 |  |  | 50 |  |  | 40 | 60 |  | Side-by-side comparisons can be good. Year by year change to output parameters in a time-lapse fashion may be interesting.
| Y | Gross MEP space per Cabinet, SF |  |  |  | 35 |  | 25 | 40 |  |  | 131.25 |  |  | 150 | 200 |  | Let us discuss once all of us are aligned on content and accuracy.
| Y | Heat recovery & reuse % |  | annual basis |  | 0% | [5 empty] | 25% |  |  | 0% | 100% |  | Only Set 1 is included. Depending on how long programming Set 1 takes, we can decide when to take on Sets 2 and 3. Maybe next year!
| Y | % of above used for water purification |  |  |  | 0% | [5 empty] | 75% |  |  | 50% | 100%
| Y | Average power cost, year 1 in $/kWH |  |  |  | 0.2 |  | 0.1 | 0.25 |  |  | 0.2 |  |  | 0.1 | 0.25
| Y | Power cost escalation per year |  |  |  | 3% |  | 2% | 4% |  |  | 3% |  |  | 2% | 4%
| Y | Revenue per kW/month, year 1 in $ |  |  |  | 500 |  | 100 | 600 |  |  | 500 |  |  | 100 | 600
| Y | Revenue escalation per year |  |  |  | 2% |  | 0% | 4% |  |  | 2% |  |  | 0% | 4%
Mk2 Optimized for mostly Air cooled cabinets
| Y | Year of Life |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
| Y | Calendar Year |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
| Y | Air Cooled | kW/Cabinet | 4.75 | 5.5 | 6.25 | 7 | 7.75 | 8.5 | 9.25 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Y | Liquid Cooled | kW/Cabinet | 20 | 21.6 | 23.328 | 25.1942 | 27.2098 | 29.3866 | 31.7375 | 34.2765 | 37.0186 | 39.9801 | 43.1785 | 46.6328 | 50.3634 | 54.3925 | 58.7439 | 63.4434 | 68.5189 | 74.0004 | 79.9204 | 86.314 | 93.2191 | 100.6767 | 108.7308 | 117.4293 | 126.8236 | 136.9695 | 147.9271 | 159.7612 | 172.5421 | 186.3455
| Y | Air Cooled Cabinets | % | 98.75% | 97.5% | 96.25% | 95% | 93.75% | 92.5% | 91.25% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90%
| Y | New+Refresh | kW/Cabinet | 4.9406 | 5.9025 | 6.8904 | 7.9097 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
| Y | Connected IT load | MW | 2.9644 | 7.083 | 12.4028 | 18.9833 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2
| Y | Newly installed cabinets |  | 600 | 600 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Y | No. of cabinets refreshed |  | 0 | 0 | 150 | 225 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
| Y | Combined Ave. | kW/Cabinet | 4.9406 | 5.4216 | 6.0336 | 6.6785 | 6.8437 | 6.9882 | 7.1147 | 7.2254 | 7.3222 | 7.4069 | 7.4811 | 7.5459 | 7.6027 | 7.6523 | 7.6958 | 7.7338 | 7.7671 | 7.7962 | 7.8217 | 7.844 | 7.8635 | 7.8805 | 7.8955 | 7.9085 | 7.92 | 7.93 | 7.9387 | 7.9464 | 7.9531 | 7.959
| Y | Installed Cabinets |  | 600 | 1200 | 1800 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400
| Y | Average PUE |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Y | Total load | MW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Y | Energy unit cost | $/kWH | 0.2 | 0.206 | 0.21218 | 0.21855 | 0.2251 | 0.23185 | 0.23881 | 0.24597 | 0.25335 | 0.26095 | 0.26878 | 0.27685 | 0.28515 | 0.29371 | 0.30252 | 0.31159 | 0.32094 | 0.33057 | 0.34049 | 0.3507 | 0.36122 | 0.37206 | 0.38322 | 0.39472 | 0.40656 | 0.41876 | 0.43132 | 0.44426 | 0.45759 | 0.47131
| Y | Energy cost | $ M | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Y | Unit revenue | $/kW/month | 500 | 510 | 520.2 | 530.604 | 541.2161 | 552.0404 | 563.0812 | 574.3428 | 585.8297 | 597.5463 | 609.4972 | 621.6872 | 634.1209 | 646.8033 | 659.7394 | 672.9342 | 686.3929 | 700.1207 | 714.1231 | 728.4056 | 742.9737 | 757.8332 | 772.9898 | 788.4496 | 804.2186 | 820.303 | 836.7091 | 853.4432 | 870.5121 | 887.9223
| Y | Revenue | $M | 17.7862 | 43.348 | 77.423 | 120.8714 | 124.6962 | 127.1901 | 129.7339 | 132.3286 | 134.9752 | 137.6747 | 140.4282 | 143.2367 | 146.1015 | 149.0235 | 152.004 | 155.044 | 158.1449 | 161.3078 | 164.534 | 167.8246 | 171.1811 | 174.6048 | 178.0969 | 181.6588 | 185.292 | 188.9978 | 192.7778 | 196.6333 | 200.566 | 204.5773
Mk2 modified and optimized for Liquid cooled cabinets
| Y | Year of Life |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
| Y | Calendar Year |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
| Y | Air Cooled | kW/Cabinet | 4.75 | 5.5 | 6.25 | 7 | 7.75 | 8.5 | 9.25 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Y | Liquid Cooled | kW/Cabinet | 20 | 23 | 26 | 29 | 32 | 35 | 38 | 41 | 44 | 47 | 50 | 53 | 56 | 59 | 62 | 65 | 68 | 71 | 74 | 77 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
| Y | Air Cooled Cabinets | % | 88% | 86% | 84% | 82% | 80% | 78% | 76% | 74% | 72% | 70% | 68% | 66% | 64% | 62% | 60% | 58% | 56% | 54% | 52% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50%
| Y | Combined | kW/Cabinet | 6.58 | 7.95 | 9.41 | 10.96 | 12.6 | 14.33 | 16.15 | 18.06 | 19.52 | 21.1 | 22.8 | 24.62 | 26.56 | 28.62 | 30.8 | 33.1 | 35.52 | 38.06 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| Y | Connected Load* | MW | 3.948 | 9.54 | 16.938 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2 | 19.2
| Y | Newly installed cabinets |  | 160 | 160 | 160 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Y | No. of cabinets refreshed |  | 0 | 0 | 40 | 60 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
| Y | Combined Ave. | kW/Cabinet | 6.58 | 7.265 | 8.1588 | 9.1217 | 9.5565 | 10.1532 | 10.9028 | 11.7974 | 12.7627 | 13.8049 | 14.9293 | 16.1406 | 17.443 | 18.8402 | 20.3351 | 21.9308 | 23.6294 | 25.4332 | 27.2541 | 28.8473 | 30.2414 | 31.4612 | 32.5286 | 33.4625 | 34.2797 | 34.9947 | 35.6204 | 36.1678 | 36.6469 | 37.066
| Y | Installed Cabinets |  | 160 | 320 | 480 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640 | 640
| Y | Average PUE |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Y | Total load | MW | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Y | Energy unit cost | $/kWH | 0.2 | 0.206 | 0.21218 | 0.21855 | 0.2251 | 0.23185 | 0.23881 | 0.24597 | 0.25335 | 0.26095 | 0.26878 | 0.27685 | 0.28515 | 0.29371 | 0.30252 | 0.31159 | 0.32094 | 0.33057 | 0.34049 | 0.3507 | 0.36122 | 0.37206 | 0.38322 | 0.39472 | 0.40656 | 0.41876 | 0.43132 | 0.44426 | 0.45759 | 0.47131
| Y | Energy cost | $ M | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Y | Unit revenue | $/kW/month | 500 | 510 | 520.2 | 530.604 | 541.2161 | 552.0404 | 563.0812 | 574.3428 | 585.8297 | 597.5463 | 609.4972 | 621.6872 | 634.1209 | 646.8033 | 659.7394 | 672.9342 | 686.3929 | 700.1207 | 714.1231 | 728.4056 | 742.9737 | 757.8332 | 772.9898 | 788.4496 | 804.2186 | 820.303 | 836.7091 | 853.4432 | 870.5121 | 887.9223
| Y | Revenue | $M | 23.688 | 58.3848 | 105.7338 | 122.2512 | 124.6962 | 127.1901 | 129.7339 | 132.3286 | 134.9752 | 137.6747 | 140.4282 | 143.2367 | 146.1015 | 149.0235 | 152.004 | 155.044 | 158.1449 | 161.3078 | 164.534 | 167.8246 | 171.1811 | 174.6048 | 178.0969 | 181.6588 | 185.292 | 188.9978 | 192.7778 | 196.6333 | 200.566 | 204.5773
Note on N8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Allowance for miss in estimate of maximum average kW/cab - actual densities being lower than the input here. Range for uncertainty can be 0%-50%
Note on AB15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Doug Asay Please check formulas
Note on C20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Single PUE number is used instead of average PUE, peak PUE, true PUE, etc. for simplicity at the moment. Will need to add those distinctions in the future.
Note on Z20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on derived formula on sheet ‘REF Capex Comparison’
Note on AB20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on derived formula on sheet ‘REF Capex Comparison’. Based on earlier research indicating that for new construction, for the same IT power liquid cooling capes costs are likely to be same or lower than for air cooling, with liquid cooling being greater in power density.
Note on C23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: True PUE includes server fan power as part of cooling plant power consumption. We assume a 0.1 average contribution toward PUE, here which can be verified further and revised. Reply: See description on REF TUE Description tab
Note on M28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This assumption needs to be verified. MEP space is likely to increase with cabinet power density, whereas liquid cooling is likely to offer MEP space savings over air cooling.
Note on G29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typically zero for air cooling
Note on M29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Heat recovery for various uses such as district heating, domestic hot water, greenhouses, water purification, etc., can be significant due to high grade (>60℃) heat available from heat rejection. More reuse opportunities exist in colder climates.
Note on M33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assuming that there is no variation in pricing between air cooled and liquid cooled cabinets per kW.
Note on C41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Expected power density is for a refresh or new cabinet installed during a particular calendar year
Note on C42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Expected power density is for a refresh or new cabinet installed during a particular calendar year
Note on C61: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Expected power density is for a refresh or new cabinet installed during a particular calendar year
Note on C62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Expected power density is for a refresh or new cabinet installed during a particular calendar year